## Tachometer FI-Converter
Tachometer / FI-Converter | [12 empty] | legend
Functional specification document (FSD) | [13 empty] | fulfilled / demonstrated (ok)
Requirement | [5 empty] | Verification Requirements |  |  | Status - Supplier: XXXXXX |  |  |  |  | not yet validated (?)
No. | Titel | Description |  | origin | Approved on | Test | Description | origin | Status | Comments / testing | References | last update |  | validation failed (x)
Environmental conditions
1.1 | Operaton Temperature | permanent | +5…55°C | IACS E10 / IEC 61131-2 (OTH3) | 2022-11-23 | Cold test: Dry heat test: Damp heat test: | 2 h @ +5°C 16h @ +55°C 2x cycles 25…55°C (2 x 24 hours) @ 95% humidity | IACS E10 | ?
1.2 | Humidity | permanent | 0…95% (no condensation) | [5 empty] | ?
1.3 | Vibration | Ampl. in all 3 dir. | ± 1 mm ± 7 m/s2 | IACS E10 (IEC 60068-2-6) | 2022-11-23 | no resonace: 90 min @ 30 Hz | during the vibration test, functional test are to be carried out | IACS E10 | ?
|  | Freq. Range | 2 … 13.1 Hz 13.2 … 100 Hz |  |  | resonance: 90 min @ each fRes
1.4 | Shock | 3 shocks |  | IEC 61131-2 | 2022-11-23 | 11 ms, min. 3 shocks | in all 3 axis, 15 g | EN60068-2-27 | ? |  |  | 2023-03-21
|  | Ampl. in all 3 dir. | 15 g
|  | Duration | 11 ms
Electrical requirements
Supply
2.1 | Supply voltage | Nominal 24 VDC Range: 20.4…28.8 VDC |  | Industrial environment, e.g., acc. to IEC 61131-2 | 2022-11-23 | Voltage variation test insulation resistance | Un +20% / -15% (test duration 30 min) test voltage 2*Un + 500 VDC, resistance > 2 Mohm test casing-each pin test shield pin - each other Pin | IEC 61131-2 IACS E10 | ? |  |  | 2023-03-21
2.2 | Power consumption | P ≤ 10 W |  |  | 2022-11-23 | Power measurement @ Tmin /Tmax | Using an adequate test equipment |  | ? |  |  | 2023-03-21
2.3 | Protection | Inverse polaritiy protection |  | avoid damage | 2022-11-23 | Check inverse GND, V+ | no device damage must occur |  | ? |  |  | 45006
Signal Input
3.1 | Sensor connection | - positive signal conductor |  |  | 2022-11-23 | Function test | Using an adequate test equipment |  | ? |  |  | 2023-03-21
|  | - negative signal conductor | [6 empty] | ? |  |  | 2023-03-21
|  | - Sensor supply for active sensors | [6 empty] | ? |  |  | 2023-03-21
|  | - Sensor cable screening | [6 empty] | ? |  |  | 2023-03-21
3.2 | Input signal | Voltage | ± 15V (passive signals) |  | 2022-11-23 |  |  |  | ?
|  |  | ~+22V rectangular pulses (active signals) pull-up concept |  | 2022-11-23 |  |  |  | ?
|  | Pulse width | ≥ 12 us (active and passive signals) |  | 2022-11-23 |  |  |  | ?
|  | Signal shape passive input signal |  |  | 2022-11-23 |  |  |  | ?
|  | Signal shape active input signal |  |  | 2022-11-23 |  |  |  | ?
|  | Noise | ≤ 1.4V |  | 2022-11-23 |  |  |  | ?
3.3 | Input impedance | Resistance: Ri ≥ 5 kOhm |  |  | 2022-11-23 | Resistance measurement Function test | Using an adequate test equipment |  | ? |  |  | 2023-03-21
|  | Capacity: Ri ≤ 1 nF | [6 empty] | ? |  |  | 2023-03-21
3.4 | Pulse triggering | Trigger and hysteresis levels must be adjustable |  |  | 2022-11-23 |  |  |  | ?
|  | Adaptive trigger is preferred |  |  | 2022-11-23 | Check inverse GND, Sig | no device damage must occur |  | ? |  |  | 45006
3.5 | Protection | Inverse polaritiy protection |  | avoid damage | 2022-11-23 | Check inverse GND, Sig | no device damage must occur |  | ? |  |  | 45006
Signal outputs
4.1 | Analogue output | Signal | 4-20 mA |  | 2022-11-23 | Function test insulation resistance | Using an adequate test equipment test voltage 500 VAC, 50 & 60 Hz, resistance > 2 Mohm test casing-each pin test shield pin - each other Pin |  | ? |  |  | 45006
|  | Accuracy | ≤ 0.5% (incl. linearity error) | [5 empty] | ? |  |  | 45006
|  | RL | ≤ 500 Ohm | [5 empty] | ? |  |  | 45006
|  | General | Potential free | [5 empty] | ? |  |  | 45006
4.2 | Open collector output | Type | passive with external pull-up |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  | Load voltage | 5 - 30 VDC | [5 empty] | ? |  |  | 45006
|  | Load current | < 25 mA | [5 empty] | ? |  |  | 45006
4.3 | Digital outputs | Amount | 2 |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  | Uout | ≥ 24 V |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  | P | ≥ 3 W |  | 2022-11-23 |  |  |  | ? |  |  | 45006
4.4 | Display | F/I converter | no display |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  | Tachometer | LED / LCD (with background ligthing) |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  |  | 5 numerals (no leading zeros, no decimal places) |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  |  | Numeral size: 12 … 20 mm |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  |  | Update interval: ≥ 0.5 s |  | 2022-11-23 |  |  |  | ? |  |  | 45006
|  |  | Reading angle: ≥ 45° (perpendicular to display) |  | 2022-11-23 |  |  |  | ? |  |  | 45006
4.5 | Protection | Inverse polaritiy protection |  | avoid damage | 2022-11-23 | Check inverse GND, Sig | no device damage must occur |  | ? |  |  | 45006
Communicaton
5.1 | Interface | Serial transmission via USB port (tbd) |  | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
5.2 | Device setting | Software must provide the following fucntions/settings: |  | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | Compatible with Windows10 and higher | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | Automated detection of the connected device | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | change the amount of pulses per revolution | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | Tigger level (if not adaptive) | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | Parameters for digital output setting | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | Analoge output setting | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | to display & evaluate values in Hz and min-1 | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | to store actual settings | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
|  |  | to load a parameter setting file and to download it to the device | HZTL650334 | 2022-11-23 | <- |  |  | ? |  |  | 45006
Mechanical requirements
6.1 | Casing material | suitable for intented applications and conditions |  |  | 2022-11-23 | Visual inspection |  |  | ?
6.2 | Protecton class | Casing | IP40 | Standard IP protection for devices fixed inside control cabinet | 2022-11-23 |  |  |  | ?
|  | Terminals | IP20 | [5 empty] | ?
6.3 | Dimensional requirement | Tachometer | 96 mm * 48 mm for panel installation | Acc. to DIN43700 | 2022-11-23 | check dimension |  |  | ?
|  | F/I transformer | DIN rail assembly | Acc. To EN50022-35 and DIN46227 |  |  |  |  | ?
6.4 | Labeling | according to drawing |  |  | 2022-11-23 | check visual label |  |  | ?
General requirements
7.1 | Operatoin manual | In English with all relevant information |  |  | 2022-11-23 |  |  |  | ?
7.2 | Packing | Device must be packed in an environmental compatible bag with all relevant tech. documents |  |  | 2022-11-23 |  |  |  | ?
7.3 | Warranty | Must be guaranteed that all requirements are fulfulled |  |  | 2022-11-23 |  |  |  | ?
7.4 | Modifications and discontinuations | Must be fulfulled according to the requirments |  |  | 2022-11-23 |  |  |  | ?
Standards
General
8.1 | CE |  |  | Product safety | 2022-11-23 | <-- | el. Saftey must be ensured, CN local standard could be accepted but must at least cover the CE requirements |  | ?
8.2 | RoHS / REACH |  |  | EU directive 2011/65/EC | 2022-11-23 | <-- |  |  | ?
8.3 | WEEE |  |  | EU directive 2012/19/EC | 2022-11-23 | <-- |  |  | ?
Conformity
9.1 | Marine Certification | acc. to DNV-GL | Certificate is mandatory | IACS / DNV-GL | 2022-11-23 | <-- |  |  | ?
|  | acc. to ABS | Certificate is optional |  | 2022-11-23 | <-- |  |  | ?
Flame retardent
10.1 | Device | no flame |  | IACS E10 (IEC 600092-101 / IEC 60695-11-5) | 2022-11-23 | <-- |  |  | ?
|  | buring part and drops must be selfextinguishable |  |  | 2022-11-23 | <-- |  |  | ?
EMC
Immunity
11.1 | Radio Frequency electromagnetic field | IEC61000-4-3 | 80..2000 MHz / 10 Vrms/m; 80% AM (1 kHz) 2.0…6 GHz / 3 Vrms/m; 80% AM (1 kHz) | IACS E10 / IEC 61000-6-2 / IEC 61000-6-4 | 2022-11-23 | <-- |  |  | ?
11.2 | Electrostatic discharge | IEC61000-4-2 | Cont. discharge +/- 6 kV Air discharge+/- 8 kV | IACS E10 | 2022-11-23 | <-- |  |  | ?
11.3 | Radio-frequency common mode | IEC61000-4-6 | 0.15…80 MHz / 10 Vrms / 80% AM (1 kHz) | IEC 61000-6-2 / IEC 61000-6-4 | 2022-11-23 | <-- |  |  | ?
11.4 | Surges | IEC61000-4-5 | Pulse rise time: 1.2us / Pulse width: 50 us ± 1 kV (line-earth) ± 0.5 kV (line-line) | IACS E10 | 2022-11-23 | <-- |  |  | ?
11.5 | Fast transients | IEC61000-4-4 | Power line: ± 2 kV, 5/50ns, 5 kHz IO Port: ± 1 kV, 5/50ns, 5 kHz | IACS E10 | 2022-11-23 | <-- |  |  | ?
Emmission
12.1 | Radiated emissions | CISR 16-2-3 | 30…230 MHz: 40 dB(uV/m) 230…1000 MHz: 47 dB(uV/m) Except: 156…165 MHz: 24 dB(uV/m) 3 m distance | IACS E10 | 2022-11-23 | <-- |  |  | ?
12.2 | Conducted emissions | CISR 16-2-1 | 10…150 kHz: 120…69 dB(uV) 150…500 kHz: 79 dB(uV) 0.5 … 30 MHz: 73 dB(uV) | IACS E10 | 2022-11-23 | <-- |  |  | ?
Reliability
13.1 | Failure rate | SN29500 | at 40°C, <4.4% for 15'000 rhrs | TB11945, ~14% / 50.000 rhrs | 2022-11-23 | calculation or verification based on field experiences |  |  | ?