5000KW光伏逆变器需求

一，方案要求：

- 产品方案需要包含完整的方案，包括硬件方案，软件方案，结构方案，外观方案等。

- 产品方案要求具有大批量可生产性。

- 产品方案必须满足以下详细的功能和性能要求。

- 产品方案具有较高的性价比。

- 外观具有一定的工业设计，更符合家庭使用的审美。

二，逆变器具备的功能：

- 产品具有LCD显示，或者手机APP直连功能。显示设备当前的所有工作状态。

- 可以通过LCD或者手机APP显示，AC输入电压，电流，功率和频率；PV输入电压，电流和功率，AC输出的电压，电流，功率和频率；电池电压，充电电压，充电电流，电池电量。

- 负载比例和过载指示。

- 电池充电放电电流设置，状态指示。

- 支持FLD，AGM和Li-ion等多种类型的蓄电池的充电。

- 产品具备USB的OTG功能。

- 产品可以记录所有的运行日志在设备内部或者上传到管理平台。

- 可以支持并网，离网和并网备份功能，并且可以通过程序设置供电优先级。

- 可以指示当前AC输入，电池，PV和AC输出之间的电能流向。

- 支持WIFI或者4G链接，可以支持设备的联网管理。

- 为BMS预留通信端口例如：CAN, RS-485 or RS-232。

- 支持多台（至少5台）设备并联使用。

- 具有电源开关，用于开启或者停止逆变器。

- 具有干接点输出功能（用于输出指示电池的状态）。

- 当设备出现故障时，可以通过LCD或者手机APP显示故障代码或者故障详情，设备具有声音告警功能：至少支持过温故障，过载故障，风扇故障，电池低电压，电池未连接，PV电压超范围，AC输入电压超范围，AC输出电压超范围，AC输出短路等告警功能。

- 设备具有过温保护，过载保护功能。

- 支持单项和三相模式。

- 具有实时时间。

- 具有PV发电的统计功能，可以按天，月，年和总的发电量统计。

三，逆变器的性能：

| PHASE | 1-phase in / 1-phase out |
| --- | --- |
| MAXIMUM PV INPUT POWER | 6000W |
| RATED OUTPUT POWER | 5600W |
| MAXIMUM CHARGING POWER | 6000W |
| GRID-TIE OPERATION |  |
| PV INPUT (DC) |  |
| Nominal DC Voltage / Maximum DC Voltage | 360 VDC / 450 VDC |
| Start-up Voltage / Initial Feeding Voltage | 110VDC / 120 VDC |
| MPP Voltage Range | 120 VDC ~ 430 VDC |
| Number of MPP Trackers / Maximum Input Current | 1 / 27 A |
| GRID OUTPUT (AC) |  |
| Nominal Output Voltage | 220/230/240 VAC |
| Output Voltage Range | 184 - 264.5 VAC or 195.5 - 253 VAC (Selectable) |
| Nominal Output Current | 24.3A |
| Power Factor | > 0.9 |
| EFFICIENCY | 96% |
| OFF-GRID OPERATION |  |
| AC INPUT |  |
| AC Start-up Voltage / Auto Restart Voltage | 120 - 140 VAC / 180 VAC |
| Acceptable Input Voltage Range | 90 - 280 VAC or 170 - 280 VAC |
| Maximum AC Input Current | 40 A |
| PV INPUT (DC) |  |
| Maximum DC Voltage | 450 VDC |
| MPP Voltage Range | 120 VDC ~ 430 VDC |
| Number of MPP Trackers / Maximum Input Current | 1 / 27 A |
| BATTERY MODE OUTPUT (AC) |  |
| Nominal Output Voltage | 220/230/240 VAC |
| Output Waveform | Pure sinewave |
| Efficiency (DC to AC) | 93% |
| HYBRID OPERATION |  |
| PV INPUT (DC) |  |
| Nominal DC Voltage / Maximum DC Voltage | 360 VDC / 450 VDC |
| Start-up Voltage / Initial Feeding Voltage | 110VDC / 120 VDC |
| MPP Voltage Range | 120 VDC ~ 430 VDC |
| Number of MPP Trackers / Maximum Input Current | 1 / 27 A |
| GRID OUTPUT (AC) |  |
| Nominal Output Voltage | 220/230/240 VAC |
| Output Voltage Range | 184 - 264.5 VAC or 195.5 - 253 VAC (Selectable) |
| Nominal Output Current | 24.3A |
| AC INPUT |  |
| AC Start-up Voltage / Auto Restart Voltage | 120 - 140 VAC / 180 VAC |
| Acceptable Input Voltage Range | 90 - 280 VAC or 170 - 280 VAC |
| Maximum AC Input Current | 40A |
| BATTERY MODE OUTPUT (AC) |  |
| Nominal Output Voltage | 220/230/240 VAC |
| Efficiency (DC to AC) | 93% |
| BATTERY & CHARGER |  |
| Nominal DC Voltage | 48 VDC |
| Maximum Solar Charging Current | 120A |
| Maximum AC Charging Current | 120A |
| Maximum Charging Current | 120A |
| GENERAL |  |
| Dimension, D x W x H (mm) | TBD |
| Net Weight (kgs) | TBD |
| INTERACE |  |
| Parallel Function | Yes, 5 units |
| Communication Port | RS485/RS232/Dry-Contact/WiFi |
| ENVIRONMENT |  |
| Humidity | 0 ~ 90% RH (Non-condensing) |
| Operating Temperature | -10 to 50ºC |